## JOB PLAN-TASKS
JPNUM | DESCRIPTION | JOBTASKID | JOB TASK DESCRIPTION | JOB TASK SEQUENCE | TASK DURATION IN HOUR
JP415001 | Air Handling Unit (Quarterly) | 10 | Inspect unit body for corrosion, defected painting or damages; clean properly and report findings . | 1 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 20 | Inspect prefilter for any defect, if defected replace immediately. | 2 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 30 | Clean remaining undefected prefilters with commercial solvent and clean with soft water. | 3 | 0:15
JP415001 | Air Handling Unit (Quarterly) | 40 | Inspect bag filters for defects, if found replace immediately. | 4 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 50 | Clean remaining undefected bag filters using a vaccum cleaner. | 5 | 0:15
JP415001 | Air Handling Unit (Quarterly) | 60 | Inspect filter frame work and casing. wire brush and paint with anti-corrosion primer. if required | 6 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 70 | Examine filter element seating for air leakge. repair and re-join filter element seating as required. | 7 | 0:05
JP415001 | Air Handling Unit (Quarterly) | 80 | Check filter element locking devices for security of fastening. adjust refit or replace defective fastenings to ensure air taightness. | 8 | 0:01
JP415001 | Air Handling Unit (Quarterly) | 90 | Inspect chilled water and hot water coils for corrosion, algae or defects, clean with commercial solvent and clean with soft water, report any finding. | 9 | 0:10
JP415001 | Air Handling Unit (Quarterly) | 100 | Inspect coil and associated piping for leakages; if found take immediate corrective action | 10 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 110 | Clean the strainer then back flush unit coil by opening the return isolating valve; coordinate with water treatment specialist forcristalization or an unusual findings. | 11 | 0:10
JP415001 | Air Handling Unit (Quarterly) | 120 | Inspect blower, blower housing and shaft for any defect, clean properly and report finding | 12 | 0:10
JP415001 | Air Handling Unit (Quarterly) | 130 | Inspect base frame and isolation mounts; take immediate corrective action for any finding | 13 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 140 | Inspect motor casing for corrosion, defected painting or damages; clean properly and report finding | 14 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 150 | Dismantle the motors ventilation fan's cover, and clean the fan; take immediate corrective action if found defected. | 15 | 0:15
JP415001 | Air Handling Unit (Quarterly) | 160 | Inspect blower front and back bearing clearance using a proper sized feeler guage | 16 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 170 | Lubricate wheel front, back bearing, and motor bearing if applicable, keep injecting grease unit all old grease has been removed. | 17 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 180 | Using a proper torque insure that all bots are tight | 18 | 0:01
JP415001 | Air Handling Unit (Quarterly) | 190 | Inspect pulleys and belts for cracks, wear and fraying, if found replace | 19 | 0:01
JP415001 | Air Handling Unit (Quarterly) | 200 | Inspect driving pulleys for security on their respective shafts. re-secure a loose pulley by tightening all security bolts and locks. | 20 | 0:01
JP415001 | Air Handling Unit (Quarterly) | 210 | Check miss-alignment of driving pulleys; rectify if incorrect and record …………………. | 21 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 220 | Measure belt tension using a proper measuring device adjust if incorrect and record ………………… | 22 | 0:01
JP415001 | Air Handling Unit (Quarterly) | 230 | Check security of driving gaurds, and ispect for corrosion or any defect; report findings. | 23 | 0:01
JP415001 | Air Handling Unit (Quarterly) | 240 | Repeat 10,11,12,13,14,15,16,17,18,19,20,21 and 22 for return blower if exist | 24 | 0:10
JP415001 | Air Handling Unit (Quarterly) | 250 | Check volume dampers for proper opening and closing, inspect for corrosion, dirt or defect; take immidiate corrective action if found then clean. | 25 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 260 | Operate the unit in automatic mode for 30 min and take immediate corrective action for any abnormal finding. | 26 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 270 | Record the blowers direction of rotation……….. | 27 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 280 | Examine for undue noise, vibration, or rattling. | 28 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 290 | Measure units noise using a proper measuring device………………. compare with recommended………………….. and previous two month………………... | 29 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 300 | Measure units vibration and compare with recommended and previous two month for the following locations,front bearing and rear bearing | 30 | 0:05
JP415001 | Air Handling Unit (Quarterly) | 310 | Repeat 26,27,28 and 29 for return blower if exist. | 31 | 0:10
JP415001 | Air Handling Unit (Quarterly) | 320 | Vent air from coils; ensure tightness of vent cock, check for leakage and adjust if necessary. | 32 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 330 | Examine at automatic operation the temperature changes at the suction thermometer ……………………and discharge thermometer……………… report steady state readings. | 33 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 340 | Examine at automatic operation the perssure changes at suction…………………….. and discharge…………………………. report steady state parameters. | 34 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 350 | Examine at automatic operation the travel of the control valve, override manually to insure free travel then release override. | 35 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 360 | Record motor's voltage, power, and electric current reading………………………… and compare with previouse two months……………………. if higher than normal turn off and report (supply and return motor) | 36 | 0:10
JP415001 | Air Handling Unit (Quarterly) | 370 | Record motor's rpm using a taco meter………………….. and compare with commissioning data (supply and return motor) | 37 | 0:05
JP415001 | Air Handling Unit (Quarterly) | 380 | Check tightness and air leaks between the different sections of the unit. replace gaskets as necessary | 38 | 0:02
JP415001 | Air Handling Unit (Quarterly) | 390 | Inspect sockets, terminal cables, sensors connections, air vents, door handlers, all units accessories and hookup report finding. | 40 | 0:12
JP415001 | Air Handling Unit (Quarterly) | 400 | Inspect drain pipes and make sure they are free from obstruction by pouring some amount of water. | 41 | 0:02
Note on A1: Author: COMING FROM THE JOB PLAN